TRE C – CLIP-IN SYSTEM
VOCI DI CAPITOLATO
SPECIFICATIONS

Voci di capitolato
I pannelli del controsoffitto CLIP-IN SYSTEM prodotti da TRE C saranno realizzati in acciaio zincato a caldo preverniciato spessore 0.6mm. La finitura dei pannelli sarà bianco RAL 9010.
Il modulo unitario misurerà 600x600x25 mm, con bordo smussato 3 mm tipo A45.
Ogni pannello sarà completamente ispezionabile e avrà superficie microforata. La foratura avrà fori diametro 1.5mm sfalsati a 45° con rapporto V/P 22%. I pannelli avranno uno scuretto non forato da 10mm sui quattro lati.
Per migliorare le prestazioni acustiche ogni pannello sarà fornito con applicazione di tessuto non tessuto fonoassorbente ignifugo applicato sul retro del peso di 60 g/m2 di colore nero.
I pannelli risponderanno alla classe di reazione al fuoco Euroclasse A1 (D.M. del 15 Marzo 2005); manterranno stabilità dimensionale anche in situazioni ambientali estreme e potranno essere installati in ambienti con elevati tassi d’umidità relativa e notevoli sbalzi termici. Per l’impiego in esterni si consiglia di contattare l’ufficio tecnico TRE C.
Ciascun pannello sarà installato ad incastro su specifica struttura di sostegno nascosta Sistema CLIP-IN prodotta da TRE C composta da profilo a triangolo tipo W_PTR_ZN, sospesa al soffitto esistente mediante agganci in acciaio zincato W_SOPTR, pendino rigido d’acciaio zincato in filo diametro 4 mm W_PEND_D4_500 e molla d’acciaio armonico W_PEND_D4_MOLL.
Lungo il perimetro, il controsoffitto verrà rifinito con apposito profilo d’acciaio perimetrale W_PL_20x40 con finitura coordinata a quella del controsoffitto. I pannelli verranno assicurati al profilo tramite molle di tenuta in acciaio armonico W_MOLL_40x20.

Specifications
The CLIP-IN SYSTEM false ceiling panels produced by TRE C will be made of 0.6mm thick pre-painted hot-dip galvanized steel. The finish of the panels will be white RAL 9010.
Each panel will measure 600x600x25 mm, with a 3 mm bevelled edge, type A45.
Each panel will be fully inspectable and will have a micro-perforated surface. The perforation will have 1.5mm diameter holes staggered at 45° with an open surface of 22%. The panels will have a 10mm non-perforated shutter on all four sides.
To improve acoustic performance, each panel will be supplied with an application of fireproof sound-absorbing non-woven black fleece applied on the back, weighing 60 g/ m2.
The panels will comply with the Euroclass A1 fire reaction class (Italian Ministerial Decree 15 March 2005); they will maintain dimensional stability even in extreme environmental situations and can be installed in environments with high relative humidity rates and notable temperature changes. For outdoor use we recommend contacting the TRE C technical office.
Each panel will be installed by interlocking on a specific concealed support structure CLIP-IN system produced by TRE C composed of a W_PTR_ZN type triangle profile, suspended from the existing ceiling using galvanized steel hooks W_SOPTR, rigid galvanized steel hanger made of 4 mm diameter wire W_PEND_D4_500 and harmonic steel spring W_PEND_D4_MOLL.
Along the perimeter, the false ceiling will be finished with a special perimeter steel profile W_PL_20x40 with a finish coordinated with that of the false ceiling. The panels will be secured to the profile using harmonic steel holding springs W_MOLL_40x20.

